## Water Main
CENTRAL COAST COUNCIL
WSA 03-2011-3.1 Water Supply Code of Australia (Sydney Water Edition 2014) and CCC Supplement to WSA
AUDITING DESIGN OF WATER MAINS
Project Name / Address:
WMA Number:
Design Consultant:
Item No. | Activity | Relevant Clause | Design Complies | Consultant Comments | CCC Comments
1 | General
1.1 | Do the drawings show an appropriate revision history, and is the design complete, checked and effectively ready for construction? | CCC Supplement |  |  |  | Yes
1.2 | Is the Australian Height Datum (A.H.D) noted on design plans? | Appendix M - Drafting Requirements |  |  |  | No
1.3 | Is the Australian Map Grid (A.M.G) / Geocentric Datum of Australia (G.D.A) noted on design plans? | Appendix M - Drafting Requirements |  |  |  | Partial
1.4 | Are Council approved Construction Notes available on the design plans. | CCC Supplement |  |  |  | N/A
1.5 | Plan assessment fees and inspection fees have been paid prior to approval of design plans? | -
2 | Do localised reticulation systems comply with manuals?
2.1 | Is Sizing of Mains satisfactory (i.e. 100mm main for 40 lots)? | WSA 3.1, Table 3.1, Table 3.2 CCC Supplement
2.2 | Is Sizing of Mains relevant for industrial / commercial zones (min 150)? | WSA 3.1, Table 3.1, Table 3.2 CCC Supplement
2.3 | Is the Design Head shown on plan and is it correct? | WSA 3.2, 3.6
2.4 | Are Hydraulic Pressure ratings correct? | WSA 3.3, 3.8
2.5 | HOLD POINT: Has the water main been designed in the correct allocation? | WSA 5.4 NSW Streets Opening Coordination Council - Guide to Codes and Practices for Streets Opening Convention CCC Supplement
2.6 | If Bored road crossings are used, is continuous pipe or single pipe joint used? (continuous pipe preferred option) | WSA 15.15
2.7 | Is Cathodic Protection used for Mild Steel Pipelines? (>10m) | WSA 4.8.5, 4.8.6 CCC Supplement
2.8 | Is there adequate clearances from other services or obstructions? | WSA 5.12, Table 5.5
2.9 | HOLD POINT: Are correct Thrust restraint details shown on mains? | WSA 3.4, 7.9, Table 7.3
2.1 | Is Horizontal Alignment adequate - including curves, thrust restraint, etc? | WSA 5.4.14, 5.12.6
2.11 | Is Vertical alignment adequate - including doglegs, thrust restraint? | WSA 5.12.6
2.12 | Does Cover meet minimum requirements? | WSA 7.4.2, Table 7.2 CCC Supplement
2.13 | Do connections to existing water assets provide note for constructor to carry out the connection under inspection by Council? | CCC Supplement
2.14 | HOLD POINT: Connections to existing water assets provide a section detail presenting method of connection. | -
2.15 | Longsection provided for construction of water mains greater than or equal to DN300 and where applicable. | WSA 9.2.2
2.16 | HOLD POINT: Longsection provided for construction of any size water mains constructed within the vicinity of a medium to high density roadway including RMS road. | -
2.17 | HOLD POINT: Does the longsection show all utilities impacting the proposed new water main (i.e. gas, power, telecom, sewer, stormwater, etc.) | -
2.18 | Is there an environmental impact (e.g. tree removal) as a result of the works. If yes, have the relevant authorities been notified of the impact? | WSA 5.1.4. 11.5
3 | Do Pipeline Assemblies comply with manuals?
3.1 | Are Valves utilised appropriately? | WSA Section 8
3.2 | Are Hydrants located at high and low points and with Council spacing Requirements (min 60m spacing)? | WSA 8.8, Appendix H
3.3 | Are Hydrant types =>300mm - valve controlled Hydrants? | WSA 8.2.10, 8.8.5
3.4 | Are Chlorination assemblies shown for mains =>225mm? | WSA 5.10.3
3.5 | Does maximum size of shutoff areas (valve spacing) comply with manuals? | WSA Table 8.2
3.6 | Do services to properties comply with manuals? | WSA 5.11 CCC Water service installation requirements CCC Supplement
3.7 | For commercial and industrial greenfield development sites, pre-tapped water services have not been designed as the final use is unknown. | CCC Supplement
3.8 | Are Cul-de-sac or Court Bowl designs adequate and comply with Council supplement? | WSA 5.2.2, Figure 5.1 CCC Supplement
3.9 | Are dead end mains fitted with a hydrant valve combination to allow for future flushing purposes and ease for future connection? | CCC Supplement
3.1 | Where shown, do flanged joints have appropriate insulation? | WSA 4.6.5, Figure 4.2
3.11 | All valves, hydrants, bends, tees and all other fittings shall be located outside of the carriageway. | CCC Supplement
4 | Do Design Plans comply with manuals?
4.1 | Are completing circuits used where appropriate? | -
4.2 | Are location of Valves installed for alternate supplies? | WSA 8.1
4.3 | Does design plan show the removal of “Tee” fittings from any Existing water main to be abandoned? | -
4.4 | Are Tappings Under Pressure utilised where possible? | -
4.5 | Are Wet Tappings used in Industrial or Commercial Zones? | WSA 5.11.2
4.6 | Are Fire services labelled appropriately and drawn differently from a CCC main? | -
4.7 | Have trench stops / bulkheads been included in the design where required and specified as per WSA requirements? | WSA 7.6.1, 7.10, 15.6, WAT-1209
4.8 | Has detectable marking tape been specified in the design drawings? | WSA 15.12
5 | Does the design comply with manuals from Operational viewpoint?
5.1 | Are there sufficient hydrants and air valves to enable charging of new mains? | WSA 8.3
5.2 | Are hydrants correctly located between valves? (i.e. hydrants on high points for air release) | -
5.3 | Are there adequate numbers and locations of valves? | WSA 8.1
5.4 | Are shut valves at zone boundaries shown and correctly drawn? | WSA 8.2.4
5.5 | Are Trunk services shown to be plugged or transferred? | -
5.6 | Are location of proposed pumps or PRV's adequate? | -
5.7 | Has there been consideration made for a minimum amount of bends being introduced to the system? | -
5.8 | Have any arial crossings been designed to WSA requirements? Has there been consideration made to future access to the pipe (i.e. platform or walkway for maintenance purposes)? Are piers placed maximum 1000mm away from pipe joints? | WAT-13010, WAT-1311, WAT- 1312
6 | Materials and Trench Design
6.1 | Are all pipe materials, pipe classes, jointing methods etc. specified on design plans and are they all approved products? | WSA Product Specifications 7.4
6.2 | Trench details provided and comply? | WSA WAT-1200 series drawings
6.3 | Are embedment types specified according to WSA standard drawings or cross section details provided? | WSA WAT-1200 series drawings CCC Supplement
6.4 | Has detectable marking tape been specified in the design drawings? | WSA 15.12 CCC Supplement
6.5 | Are there wet or poor ground conditions? If yes, have detailed foundation conditions been specified in the design drawings? | WSA 5.1.5, 7.5, 7.7.3, SW28
6.6 | Has a specialist geotechnical assessment been made (i.e. where reasonable doubt of suitability of ground) | -
6.7 | Has adequate trench design been made and relevant details provided? | -
6.8 | Have structural computations for the water pipe trench design been provided for water mains 450mm or larger? | -
6.9 | Have adequate details been provided for trenchless construction? | WSA 5.4.9, 5.4.11, 5.5
6.1 | Has concrete encasement been considered in the design where applicable? Has the relevant backfill specification been provided or drawn? | WSA 7.6
7 | Existing and Abandoned Assets
7.1 | Are details of treatment for assets that are to be abandoned included on the drawings (i.e. any existing AC mains to be removed if less than 10m is disused, greater than 10m to be left in the ground and noted in the design plans)? | CCC Supplement
7.2 | Existing surface fittings have been located and designed out of future vehicle access crossings and roadways. | CCC Supplement
8 | Other Items
8.1
8.2
8.3
8.4
8.5
8.6
8.7
8.8
8.9

## Gravity Sewer Main
CENTRAL COAST COUNCIL
WSA 02-2002-2.2 Sewerage Code of Australia (Sydney Water Edition 1, Version 4) and CCC Supplement to WSA
AUDITING DESIGN OF GRAVITY SEWER MAINS
Project Name / Address:
WMA Number:
Design Consultant:
Item No. | Activity | Relevant Clause | Design Complies | Consultant Comments | CCC Comments
1 | General
1.1 | Do the drawings show an appropriate revision history, and is the design complete, checked and effectively ready for construction? | CCC Supplement |  |  |  | Yes
1.2 | Is the Australian Height Datum (A.H.D) noted on design plans? | Appendix SW3 - Drafting Requirements |  |  |  | No
1.3 | Is the Australian Map Grid (A.M.G) / Geocentric Datum of Australia (G.D.A) noted on design plans? | Appendix SW3 - Drafting Requirements |  |  |  | Partial
1.4 | Are Council approved Construction Notes available on the design plans. | CCC Supplement |  |  |  | N/A
1.5 | Plan assessment fees and inspection fees have been paid prior to approval of design plans? | -
2 | Do localised reticulation systems comply with manuals?
2.1 | HOLD POINT: Are all sewers aligned and offset as per CCC Water requirements? (located minimum 1m from front boundaries of properties; located only in road reserves for industrial/commercial areas). | WSA 4.2.3, 4.3.2 CCC Supplement
2.2 | Are all easements shown and do they comply with CCC Water requirements? | WSA 4.2.5, 9.2.2 CCC Supplement
2.3 | HOLD POINT: Are all sewers located clear of the zone of influence of structures, or if not possible, has detailed analysis been undertaken and appropriate protection been specified? Has a structural detail been provided showing zone of influence and pier detail in reference to the sewer main? | WSA 4.3.4, 4.4.4 CCC building in proximity to water and sewer pipelines procedure
2.4 | Are all curved sewers appropriately designed? (correct materials, minimum radius requirements, method of achieving curve, sufficient set out details etc.). Note, curved sewers only accepted in exceptional circumstances. Justification shall be provided to CCC Water Assessment Team and approval given for use of curved sewer. | WSA 4.3.7, 17.3.2 CCC Supplement
2.5 | Is minimum cover achieved on all pipes? | WSA 4.6.3
2.6 | HOLD POINT: Has a coordinated services plan been provided (i.e. plan or longsection indicating location for all intersecting services)? | -
2.7 | Are minimum horizontal / vertical clearances from other services achieved? | WSA 4.4.5
2.8 | Do any sewers cross over water mains? Sewer should always be located below the water main. | WSA 4.5.5.2
2.9 | Does the design include details to ensure no cross-contamination can occur between the sewer and the water main? | WSA 4.5.5.2
2.1 | Are sewers concrete encased when crossing underneath greater than or equal to DN375 stormwater pipes? | WSA Table 4.2 (Note 7)
2.11 | Does the alignment of the pipeline cross roads at right angles? | WSA 4.3.2, 4.3.3
2.12 | Is the proposed route crossing private property which requires owners consent? The developer is to obtain the permission prior to plan approval. | -
2.13 | HOLD POINT: Is the design consistent with the DA approved plans? | -
2.14 | Is there an environmental impact (e.g. tree removal) as a result of the works. If yes, have the relevant authorities been notified of the impact? | CCC Supplement
3 | Maintenance Holes
3.1 | Are all maintenance structures numbered in accordance with CCC MH numbering system? If not sure, request from Council. | -
3.2 | Does the distance between maintenance structures comply with standards? | WSA 6.3 CCC Supplement
3.3 | Are maintenance structures shown at all the locations required by the standards, and has an appropriate type of structure (MH, MC) been nominated? | 6.2, 6.7, Table 6.1 CCC Supplement
3.4 | Are minimum clearances to other structures/buildings achieved? | WSA 6.4 CCC building in proximity to water and sewer pipelines procedure
3.5 | Are correct diameters of maintenance holes nominated on design plans (i.e. 1050mm for MH's)? | WSA 6.6.4
3.6 | Is the maintenance hole cover class noted on design plans as Class D for all applications? Watertight and gastight covers specified for all maintenance holes. (i.e. Gatic bolt down lids). | WSA 6.6.9 CCC Supplement
3.7 | Is the area subject to flooding, water charged ground or areas that may become water charged? Where there is significant risk of surcharge use cast in-situ MH's only. | WSA SEW-1300-V
3.8 | Are all cover levels of maintenance structures 150mm above the 1 in 5 year storm event level? | WSA 6.6.9
3.9 | Are the locations of all pre-cast manholes in accordance with standards? | WSA 6.6.2, 6.6.3 CCC Supplement
3.1 | HOLD POINT: Are the MH base designs in accordance with standards (i.e. greater than 30 degree bend not permitted in MC's, no high level inlets permitted in MC's)? | WSA 6.6.6 CCC Supplement
3.11 | Personnel access ladders and step irons not designed for new maintenance structures. | CCC Supplement
3.12 | Is the grading through maintenance holes in accordance with standards? (min 30mm, effect of large deflections and steep grades, soffit to soffit design for different size pipes, etc.) | WSA 4.6.6
3.13 | Are guidance notes provided to the contractor for excavation next to existing manholes/structures to preserve stability during construction? | -
3.14 | Are details of connections for new sewer pipes to all existing manholes provided? (pipe invert levels, angles between pipes, stepirons, access openings, and base details). Plans and section(s) to be included. | WSA 6.5, 6.6.6, 9.2.3(i)
4 | Hydraulic Design
4.1 | HOLD POINT: Has the sewer been adequately sized and the correct pipe diameters specified in accordance with standards? | WSA 4.5.4, 4.5.5 CCC Supplement
4.2 | Does the grade of each pipe comply with standards? | WSA 4.5.4, 4.5.5, 4.5.7
4.3 | Have trench stops / bulkheads been provided where required? | WSA 8.1 CCC Supplement
4.4 | Is the velocity through the pipe below 3 m/s in accordance with the standard? | WSA 4.5.9
4.5 | Is the energy dissipated in the maintenance hole, and does the design incorporate measures to prevent hydraulic jumps? | WSA 4.6.6.5
4.6 | Where necessary, has ventilation been provided in accordance with the standard? | WSA 7.5
5 | Materials and Trench Design
5.1 | Are all pipe materials, pipe classes, jointing methods etc. specified on design plans and are they all approved products? | WSA Product Specifications 7.4 CCC Supplement
5.2 | Trench details provided and comply? | WSA 8.5, 8.6, 8.9, Tables 30.1, 30.2, 30.3, and 30.4 (commentary on SEW-1200 Drawing Series) Flexible pipes: AS/NZS 2566.1 Part 1, AS/NZS 2566.1 Part 1 - Commentary, AS/NZS 2566.2 Part 2 RIGID PIPES: AS/NZS 3725, AS/NZS 3725 - Commentary, AS 4060 CCC Supplement
5.3 | Are embedment types specified according to WSA standard drawings SEW-1202 to SEW-1205 or cross section details provided? | WSA 8.0, 30.2 WSA SEW-1202 to SEW-1205 CCC Supplement
5.4 | Has detectable marking tape been specified in the design drawings? | WSA 15.12 CCC Supplement
5.5 | Are there wet or poor ground conditions, or any sewers greater than DN 450? If yes, have detailed foundation conditions been specified in the design drawings? | WSA 8.5
5.6 | Have adequate details been provided for trenchless construction? | WSA 7.6, 32.3 (commentary on drawings for buried crossings)
6 | Property Branches / Connections
6.1 | Are all properties provided with a property branch/connection, and is the type of branch/connection nominated on design plans? | WSA 5.8, 6.6.4, 9.2.3(i) CCC Supplement
6.2 | Is the depth for property connections, junctions and end fittings in accordance with the standard? | WSA 4.6.5, 5.4 CCC Supplement
6.3 | Do all property branch inspection points terminate 1500mm from any building lines or other structures? | CCC building in proximity to water and sewer pipelines procedure
6.4 | Are water seals (i.e. boundary traps) specified where required (i.e. commercial areas, etc) | WSA 7.2 CCC Supplement
6.5 | HOLD POINT: Has the sewer and all respective property services been designed sufficiently deep to drain the entirety of each lot? | -
6 | Sewers equal to or greater than DN300
6.1 | Are self cleansing/slime stripping velocities achieved at PDWF? | WSA 4.5.7.1
6.2 | Are any sewers surcharging under 1 in 5 year floods (i.e. PWWF)? | -
6.3 | Are property connections only on sewers 225mm in dia. and less? | WSA 5.2
6.4 | Has a specialist geotechnical assessment been made (i.e. where reasonable doubt of suitability of ground or for any sewers >DN450)? | WSA 8.6.1
7 | Abandoned Assets
7.1 | Are details of treatment for assets that are to be abandoned included on the drawings (i.e. any existing AC mains to be removed if less than 10m is disused, greater than 10m to be left in the ground and noted in the design plans)? | WSA 4.5.7.1 CCC Supplement
8 | Railway / Freeway Crossings / Deep Pipes
8.1 | Are there any railway crossings or freeway crossings? | -
8.2 | Are all maintenance structures located out of the railway/freeway reserve? | -
8.3 | Are structural computations provided for maintenance structures deeper than 6.0m? | Commentary on SEW-1300 series drawings - maintenance structures - 31.11
8.4 | Has a ground conditions (geotech) report been provided where sewers are greater than 5m in depth? | -
9 | Other items
8.2
8.3
8.4
8.5
8.6
8.7
8.8
8.9

## Pump Stations
CENTRAL COAST COUNCIL
Sewage Pumping Station Code of Australia WSA 04-2005
AUDITING DESIGN OF A PUMPING STATION
Project Name / Address:
WMA Number:
Design Consultant:
Item No. | Activity | Relevant Clause | Design Complies? | Consultant Comments | CCC Comments
1 | General
1.1 | Do the drawings show an appropriate revision history, and is the design complete, checked and effectively ready for construction? | WSA 15.0 Design Documentation and Drawings |  |  |  | Yes
1.2 | Is the Australian Height Datum (A.H.D) noted on design plans? | WSA 15.0 Design Documentation and Drawings |  |  |  | No
1.3 | Is the Map Grid of Australia (MGA) noted on design plans? | WSA 15.0 Design Documentation and Drawings |  |  |  | Partial
1.4 | New and existing assets clearly shown on drawing. | WSA 15.0 Design Documentation and Drawings |  |  |  | N/A
1.5 | Existing and new water, communications, electricity and gas services shown on plan | WSA 15.0 Design Documentation and Drawings
1.6 | Vehicle Access - truck to be able to back up to wet well and bypass pump insertion openings. Minimum 4m width. | WSA 5.2.5, 26.0, SPS-1200 Series
1.7 | Vehicle turning - Crane truck to be able to turn around and leave site forwards. Turning circle to be provided for nominated vehicle type | WSA 5.2.5, 26.0, SPS-1200 Series
1.8 | Has there been consideration made for the access road to the site (if staged subdivision, how will maintenance trucks access the site)? | WSA 5.2.5, 26.0, SPS-1200 Series
1.9 | Site drainage - shown on drawings and complies with WSA standards | WSA 2.11 3.8.2, 12.1.5 SEW-1205
1.1 | Water service with RPZD - Water service to be minimum DN50 up to the hydrant and DN20 between hydrant and main cock. Main cock to PS to be DN20. Is there a note on the drawings to apply for new water supply to the pumping station (i.e. backflow prevention device) if it is an existing water main? | WSA 12.1.2
1.11 | RPZD on water service - RPZD to be DN50 if new. If water is to be available in a new building structure, then second RPZD to be provided. | WSA 12.1.2
1.12 | Hydrant - spring type and located close to wet - well | WSA WAT-1409
1.13 | External lighting - shown on site plan | WSA 12.1.4 AS4282
1.14 | Fencing - if agreed to have (any existing fencing shown on plan and reinstated post construction) | WSA 12.3
1.15 | Flood Level - 100 year flood level to be shown on all sectional elevations or note stating that the site is not subject to flooding | WSA 5.2.3
1.16 | Land acquisition details - survey coordinates of new acquisition to be shown where required | -
1.17 | Design life - designed according standards and shown on plans | WSA 1.6.2
1.18 | Is there an environmental impact as a result of the works. If yes, have the relevant authorities been notified of the impact? | WSA 19.5, 19.6
2 | Inlet MH
2.1 | Clearance to insert bypass pump (if no separate emergency storage) is minimum 1000mm diameter clear of any openings | WSA 5.3.2
2.2 | Low-level fill/drain line connecting inlet MH to additional emergency storage - Size to be not less than size of inlet line to wet-well. IL at inlet MH to be minimum 150 mm above obvert of outlet of inlet MH. | WSA 5.6.2
2.3 | Connecting pipe to additional emergency storage – High-level fill line - Size to be not less than size of inlet line to wet-well. Inlet MH end of line to be flanged. Require 150 mm clearance between flange and structure. | WSA 5.6.2
2.4 | Connecting pipe to wet-well - Highlevel fill line - Size to be not less than size of inlet line to wet-well. Inlet MH end of line to be flanged. Require 150 mm clearance between flange and structure | WSA 5.6.2
2.5 | Connecting pipe to emergency relief gas check MH (if emergency relief is off inlet) - Obvert of pipe at inlet MH to be a minimum of 300 mm below the weir crest level where possible. Size of pipe to be equal to or greater than the inlet line into the wet-well. | WSA 5.6.4
2.6 | Scum baffle on emergency relief pipe (if that pipe is off inlet MH) - Baffle to extend 50 mm above and 300 mm below pipe outlet. Note: if obvert of connecting pipe is below the weir-crest level, then no need for scum baffle in inlet MH. | WSA 5.6.4
2.7 | Personnel access ladders and step irons not to be installed in new stations. | WSA 5.6.2.4
2.8 | Are the covers in accordance with CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020 and are they arranged in a practical manner? | CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020
2.9 | Manhole material choice of pre-cast (<6m height) or cast in-situ (any height) to be made by Constructor to meet WSA requirements. If pre-cast concrete design is selected, note made to provide additional treatment of external joints by using approved wrapping system and internal joints by using epoxy coating. | -
2.1 | Location of Inlet MH (if new) To be minimum of 3 m away from edge of wet-well or else be integral part of wet-well | WSA 5.3.1
2.11 | Permanent survey marker and survey label plate | SPS-1508
3 | Wet Well
3.1 | Is the Pump Station a Package Pump Station? Confirmed on drawings. | -
3.2 | Top of wet-well - Slab/roof level of wet-well to be higher than 100 year flood level and 500mm above estimated max groundwater table. | WSA 5.2.3
3.3 | Inlet valve - Valves ≤DN 450 to be RSV gate type. Sizes >DN 450 to be knife gate In restricted spaces, knife gate valves may be used for sizes ≤DN 450 Consider need for support under valve/pipe Does the penstock (Knife gate Valve) comply with WSA requirements? | WSA 5.3.3 WSA PS-266
3.4 | Inlet line drop tube to end minimum of one pipe size above the cut-out level. SS preferred over DI. | WSA 8.7.2
3.5 | Valve spindle is designed vertical and access provided | SPS-1508
3.6 | Wet-well floor - for new wet-wells, provide self-cleansing benching all around | WSA 5.4.6 SPS-1300 & SPS-1301
3.7 | Induct vent located 1 m above O/F level | WSA 5.5.1
3.8 | Educt vent Pipe size to be not less than DN 150 or half the size of the inlet line to the wet-well (whichever is the larger). Locate as close as possible to top slab and connect to educt vent shaft. | WSA 5.5.3
3.9 | Induct / educt vent position not to permit short-circuiting and not to obstruct laying of access cover flat on ground | -
3.1 | Inlet line (including valve) from inlet MH - On roof above inlet valve show standard surface box. Show also spindle support brackets. Puddle flange should be provided at the wall penetration. | WSA 5.4.1, 9.1.3 SPS-1301
3.11 | Low-level line from emergency storage - Size to be not less than size of inlet line from Inlet MH to wet well. Wet-well end of line to have isolating valve. | -
3.12 | Discharge pipe lengths on material schedule (new stations) - Need to identify one short piece (closing pipe) as 'cut to suit' - or use packer flanges | -
3.13 | Discharge pipe work (existing stations) - Need to identify and notes to state 'Make good existing pipework'. | -
3.14 | Orientation of discharge pipe work - Minimise number of bends | -
3.15 | Sump - Confirm sump shown, located between pumps. For new wetwells, size to be 400 mm sq by 150 mm deep. | WSA 5.4.6
3.16 | Hydraulic flush valve - To be fitted to at least one unit where pumps are ≤50 kW. Above 50 kW motor size, need to review use of separate mixer or return flush pipe off main. | WSA 5.12
3.17 | Person access cover - Show ladder tie points, safety harness points etc. Show also ability for person entry and egress, the mass of each cover, its unobstructed operation in opening the cover, etc. | WSA 5.6.2.4 CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020
3.18 | Pump access and electrical covers to be aligned above pumps and to provide adequate clearance when flushing valve is fixed to pump. Has a flushing valve been incorporated into the design? | WSA 5.6.2.4, 6.7.1 CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020
3.19 | Permanent survey marker and survey label plate to be located on wet-well roof slab. | SPS-1508
3.2 | Guide rails - designed as per CCC SPS Aluminium Lids Standard Drawing requirements, and to allow removal of pumps through access cover. | CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020
3.21 | Operating levels - Show levels and weir crest level. | -
3.22 | Repainting any existing pipe and metalwork which is to remain to be noted on drawings. Notes to detail painting requirements. | -
3.23 | Existing wet-well covers to be sealed | -
3.24 | Has a minimum of 4 hrs @ PDWF emergency storage been provided between high level alarm and spill alarm? | -
3.25 | Does internal coating of concrete surfaces comply with CCC standard (International Polybrid 705-E)? | WSA 5.6.2
3.26 | Are the covers in accordance with CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020 and are they arranged in a practical manner? | CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020
3.27 | Has the wet well been designed based on minimum flow rates identified in WSA? (i.e. "small pumping station" < 90l/s)? Is the wet well diamater greater than the minimum of 2m? | WSA 5.4.1, 5.4.2
3.28 | Do the Cut-in/Cut-out volumes comply with WSA requirements? | WSA 5.4.3
3.29 | If pump flow rate designed to be over 30l/s, do wet well washers comply with standards? | WSA 5.4.7
3.3 | Does the Top Slab incorporate all below ground structures? | WSA 11.2.7
3.31 | Has the concrete strength been specified and does it comply with WSA requirements? | WSA 11.2.2.2
3.32 | Is there sufficient clearance from overhead powerlines for maintenance purposes? If powerlines are in the vicinity of the new PS, incorporate into the safety in design. | WSA Appendix C
3.33 | Fixed ladders have not been included in the design of storage structures. | WSA 5.6.2.4
3.34 | Do all pipework comply with WSA requirements (i.e. min dia. = 100mm)? | WSA 9.0
3.35 | Valve and pipe support blocks shown where required (i.e. all valves designed to have concrete blocks) | WSA 9.3.4
3.36 | Does the pump well inlet pipe comply with WSA requirements and is the inlet drop pipe submerged? (i.e. 150mm above cut out level) | WSA 5.4.1, 8.7.2
3.37 | Are all pumps, pipeworks and fittings approved products? | WSAA Product Specifications fo Products and Materials - Version 4
3.38 | Detention times < 2 hours | WSA 2.8.2, 5.4.5, Appendix D
3.39 | Davit arm system designed to CCC requirements | GCC DWG S344 - Sewerage Pumping Station Standard Davit Mounting Details
4 | Pumping Units
4.1 | Pump selection - Motor size to be minimum of 15% in excess of total power drawn at flooded wet-well duty point. With chosen motor, pump not to stall at any point on performance curve. | WSA 6.6.3
4.2 | Standard - Ensure unit complies with WSA 101-2008 | WSA 101-2008
4.3 | Guide rails - Show distance from edge of access cover to centre of guide rails | -
4.4 | Pump mounting - Show minimum permissible distance between base of pump and wet-well floor | WSA 6.6.6
4.5 | Pump and motor capacity - Details to be shown on drawing | WSA 6.6
4.6 | Pump pedestal - Installation details to be shown in notes. | -
4.7 | Taper on discharge line - Any tapers next to pump footstep bend to be eccentric | -
4.8 | Pump Cable hooks detail and location shown on drawing | -
5 | Valve Chamber | -
5.1 | Chamber size - Pipework clearances to be as per WSA Code and relevant drawing(s) Pipe set-out within valve chamber - Dimensions to be shown on drawings | WSA 9.3.2
5.2 | Height of the pipe work above the floor minimum of 300 mm to underside of flanges | WSA 9.3.2
5.3 | Valve sequence - In direction of flow, sequence to be load bearing dismantling joint, reflux valve then isolating valve | WSA 9.3.2, 9.3.3
5.4 | Double isolation valve - to be downstream of any dismantling joint(s) | WSA 9.3.2, 9.3.3
5.5 | Valve extension spindles - to be provided with support brackets and to finish within 50mm of underside of covers | WSA 9.3.2
5.6 | Valve support blocks - Concrete support blocks to be provided under valves | WSA 9.3.4
5.7 | Scour line - Scour stop valve to be positioned next to branch off tee to avoid/minimise solids accumulation | WSA 10.9.5
5.8 | Drain line - Outlet to be fitted with a 'Duck bill' type valve. Inlet to be fitted with diamond grate or equivalent mesh cover (note on general arrangement). Benching to be flush with grating openings. | WSA 9.3.2
5.9 | Dismantling joints to be thrust bearing type only. | WSA 9.3.3
5.1 | Puddle flanges - Provide at all wall crossings. | WSA 9.1.3
5.11 | Pipework support to be provided for “camlock” quick-disconnector riser pipe when valve chamber depth >2 m | -
5.12 | Personnel access ladders and step irons not to be installed in new stations. | WSA 5.6.2.4
5.13 | By-pass pump connection point Male “camlock” quick-disconnector type coupling with isolating valve and reflux valve (reflux valve in horizontal position). DN 10 SS bleed valve at base of coupling (outlet facing floor of chamber). All valves (stop, reflux, bypass and bleed) to be operable without having to enter chamber. Isolating valve on bypass line positioned next to branch off tee to avoid solids accumulation. Provide separate hinged cover to access by-pass coupling without having to open all covers. Distance from top of by-pass coupling to underside of valve chamber cover to be ≤50 mm. | WSA 9.2.3
5.14 | Chamber covers and access covers - Provide hinged covers, including separate hinged opening to access “camlock” quick disconnector type coupling | CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020.
5.15 | Covers comply with CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020. | CCC Sewer Pumping Station Aluminium Lids Standard Drawings 2020.
5.16 | Pressure tapping points - Provide DN 10 SS tapping upstream of each reflux valve and one downstream of rising main double isolation valve. Ensure 150 mm min clearance from flanges/ walls. | WSA 9.3.5
5.17 | Is the valve chamber self-draining? | WSA 9.3.2
5.18 | Are all valves anti-clockwise closing? | -
6 | Electrical Equipment
6.1 | Kiosk - position and orientation to be 100mm above 100 year flood level To face wet-well with an east/west orientation. To allow doors to open fully. To have minimum of 1500 mm clear space in front and 900. mm clearance on both sides of kiosk (for MDF and generator connections) | WSA 5.2.3
6.2 | Electricity metering panel - To be positioned so that no entry is required into confined spaces. Not to be located inside a building. | WSA 5.2.3
6.3 | Telecommunications pit - to be located within 5 m of kiosk. | -
6.4 | Level sensors - Details to be shown only on electrical drawings | WSA 8.8.5
6.5 | Float switches - Details to be shown only on electrical drawings | WSA 8.8.6
6.6 | Buoyancy switches Details to be shown only on electrical drawings | WSA 8.8.6
6.7 | Level sensors in stilling tubes + ultrasonic level sensors - Details to be shown only on electrical drawings | WSA 8.8.5
7 | Miscellanous
7.1 | Location of pumps in relation to access covers - Dimensions to be shown on drawings | -
7.2 | Level sensing instruments - Support details to be shown on drawings | WSA 8.8.5
7.3 | Materials schedule - Numbers and description to match what is shown in drawings Numbers not to be duplicated | WSA 4.0
7.4 | Pipe connection details - to be specified in notes. | -
7.5 | Emergency relief headwall - Scour protection of headwall to be specified in notes. | WSA 5.6.4
7.6 | Does the emergency relief structure comply with the EPA protocol guidelines and standards? Flap gates and trap for fats included in design? | WSA 5.6.4
7.7 | MHs and inlet MH - Standard Drawings in WSA 02 Sewerage Code of Australia to be referenced as appropriate to diameter and depth of sewer | WSA 02 Sewerage Code of Australia
7.8 | Signage requirements to be specified in notes (i.e. Working at Heights, Confined Spaces, etc). | WSA 2.14
7.9 | Electricity supply for by-pass pumping - If preferred emergency by-pass location (i.e. Inlet MH or emergency storage) is more than 10 m from kiosk, an additional electrical connection to be provided within that limit. | -
7.1 | Electrical and civil/mechanical drawings - To be consistent with each other | -
7.11 | Materials schedule - Bleed line at by-pass to be called up as "DN 10 tapping with SS ball valve and pipe” Tapping points to be called up as "DN 10 tapping with SS ball valve" By-pass quick disconnector couplings to be called up as "DN 100 flanged male camlock with dust cap; type 633LA” For pipes that include puddle flanges, show total length, length from puddle flange to each end and whether pipe ends with a flange or spigot | WSA 4.0
7.12 | Landscaping - no lawns permitted. Flora chosen that suits the area. | WSA 5.2.6
8 | Other Items
8.1
8.2
8.3
8.4
8.5
8.6
8.7
8.8
8.9

## Pressure Sewer
CENTRAL COAST COUNCIL
Pressure Sewerage Code of Australia WSA 07-2007-1.1
AUDITING DESIGN OF PRESSURE SEWERS
Project Name / Address:
WMA Number:
Design Consultant:
Item No. | Activity | Relevant Clause | Design Complies | Consultant Comments | CCC Comments
1 | General
1.1 | Do the drawings show an appropriate revision history, and is the design complete, checked and effectively ready for construction? | - |  |  |  | Yes
1.2 | Is the Australian Height Datum (A.H.D) noted on design plans? | - |  |  |  | No
1.3 | Is the Australian Map Grid (A.M.G) / Geocentric Datum of Australia (G.D.A) noted on design plans? | - |  |  |  | Partial
1.4 | Are Council approved Construction Notes available on the design plans. | - |  |  |  | N/A
1.5 | Plan assessment fees and inspection fees have been paid prior to approval of design plans? | -
1.6 | New Sewer assets shown in bold or colour and existing assets shown in faded or grey colour clearly on drawing. | -
2 | Design of Pressure Sewer
2.1 | Are all pressure sewers located within road reserves and easements, and aligned as per CCC Water requirements? | WSA 1.5.3, 3.7
2.2 | Is minimum and maximum (1.5m) cover achieved on all pipes? | WSA 3.2
2.3 | Do offset's of the pressure sewer comply with standards? | WSA 3.12, 3.13, Table 3.2
2.4 | Is a longitudinal elevation shown on the design drawings with levels referenced to AHD? Are future surface levels shown if they are to be adjusted later (e.g. embankment). Are existing services shown on the longsection drawings? | WSA 3.3
2.5 | Are minimum clearances from other services achieved? | Table 3.1
2.6 | Are there any railway or freeway crossings? Is the pipeline designed at 90 degree to the railway or freeway reserve? Are all fittings located out of the railway or freeway reserve? | WSA 3.8, 3.12.5
2.7 | Is there an environmental impact (e.g. tree removal) as a result of the works. If yes, have the relevant authorities been notified of the impact? | WSA 3.6
2.8 | Rising main(s) - Thrust blocks/thrust pressures to be shown on drawings | WSA 18.7
2.9 | Are trenchstops / bulkheads been included in the design where required and specified as per WSA requirements? | WSA 9.1.1, 18.4, WAT-1209
2.1 | Are backfill design specifications provided or referred to WSA code drawing or relevant standards? | WSA Drawing PSS-1000, PSS-1001
2.11 | Has a ground conditions report been provided where necessary? | WSA 3.6.1, 9.1.1
2.12 | Have adequate details been provided for trenchless construction (i.e. type of excavation method, size of casing pipe, details grouting material, etc? | WSA 3.13, 18.5, PSS-1002, PSS-1003, PSS-1004
2.13 | Have any arial crossings been designed to WSA requirements? Has there been consideration made to future access to the pipe (i.e. platform or walkway for maintenance purposes)? Are piers placed maximum 1000mm away from pipe joints? | WAT-13010, WAT-1311, WAT- 1312
2.14 | Are details of treatment for assets that are to be abandoned included on the drawings (i.e. any existing AC mains to be removed if less than 10m is disused, greater than 10m to be left in the ground and noted in the design plans)? | WSA 3.14
3 | Hydraulic Design
3.1 | Are the correct pipe diameters specified in accordance with the works agreement? | WSA 4.5.2, 4.5.3
3.2 | Are all pipe materials, pipe classes (PN16), pipe colour, tracer wire, jointing methods etc. specified on design plans and are they all approved products? | WSA 10.0
3.3 | Are duplicate mains used where necessary? | -
3.4 | Does the design verify that the pipe class meets the design pressures? | WSA 9.2
3.5 | Do the materials and fittings specified on the plans appear in the on the WSAA approved products list? | WSA Product Specifications 7.4
3.6 | Are the types of valves used noted on the plan? | WSA 5.4, 5.5, 10.0
3.7 | Are the valves in the appropriate location in accordance with WSA Specifications? | WSA 5.4, 5.5
3.8 | Are the valves anti-clockwise closing and noted on the plan? | -
3.9 | Does the plan include lockable flushing assemblies? | WSA 5.6
3.1 | Are the high and low points met in accordance with the WSA specifications? | WSA Appendix A
| Is the discharge manhole designed to WSA standards? Is the type of manhole construction specified on the drawings (i.e. cast in-situ or polypropylene)? Does the design specify use of International Polybrid 705-E coating internally for concrete maintenance hole. | SEW-1300, SEW-1301
3.11 | Does the outlet discharge into a Manhole and does the plan detail how the connection is to be made? | WSA SEW-1313
3.12 | Does the design of the discharge manhole incooporate internal coating of concrete surfaces and comply with CCC standard (International Polybrid 705-E)? | WSA 3.15
3.13 | Does the design of the discharge manhole prevent turbulent flow? | WSA 2.8
3.14 | Does the design avoid the use of 90 degree deflections? | -
3.15 | Where necessary, has ventilation been provided in accordance with the standard? | WSA02-2002-2.2. Sydney Water Edition Clause 7.5
4 | Design of Property Branches / Connections
4.1 | No issues have been identified Property Branches/Connections? | WSA 6.0
4.2 | Are all properties provided with a property branch/connection and is the type of branch/connection nominated on design plans? | WSA 6.1
4.3 | Where a service connection is not required at this stage, will the alignment allow them to be possible in the future? | WSA 6.3
4.4 | Are ball valves used at the property connection point? | WSA 5.4
4.5 | Collection / pump unit type confirmed on drawings? | WSA 7.0
4.6 | Property discharge assembly confirmed (i.e. plan and / or section view drawing of fittings shown?) | WSA 8.0
5 | Other Items
5.1
5.2
5.3
5.4
5.5
5.6
5.7
5.8
5.9